## About
IECCpUAEU Industrial Equipment Capital Cost per Unit Annual Energy Use
Sources: | Industrial heat pumps cost per unit heat delivered
Emerson
2011
Industrial Heat Pumps
https://climate.emerson.com/documents/vilter-heat-pump-white-paper-en-us-5411194.pdf
Industrial heat pump efficiency
Arpagaus et al.
2018
High temperature heat pumps: Market overview, state of the art, research status, refrigerants, and application potentials
https://www.sciencedirect.com/science/article/pii/S0360544218305759
Figure 8
Natural gas boiler costs
NREL
2017
Electrification Futures Study: End-Use Electric Technology Cost and Performance Projections through 2050
https://www.nrel.gov/docs/fy18osti/70485.pdf
Page 64, Table 17
Three fuel type industrial boiler costs
IRENA
2016
Remap Technology and Performance Assumptions (for year 2030)
https://www.irena.org/-/media/Irena/Files/REmap/IRENA_REmap_2030_technology_cost.xlsx
Hydrogen boiler capital cost price ratio
E3
"Achieving Carbon Neutrality in California (Revised Report): 2045 Abatement Cost Estimates"
2020
https://ww2.arb.ca.gov/sites/default/files/2020-09/e3_cn_draft_report_supp_data_aug2020.xlsx
Natural gas-fired chillers
EnergistX
undated
500 Ton Natural Gas-Fired Absorption Chiller replacement of Aged Centrifugal Electric Chiller
https://enrgistx.com/natural-gas-fired-chillers/
Electric chillers
Florida Power & Light
undated
Water-Cooled Chillers
https://www.fpl.com/content/dam/fplgp/us/en/business/save/programs/pdf/water-cooled-chillers-primer.pdf

## Boilers
Industrial heat pumps
For electricity in the "boilers" end use, we use industrial heat pumps rather than electric boilers because industrial heat pumps
are more efficient and are therefore recommended over electrical boilers wherever practical.
| Annual heat delivered (MMbtu) | Capital Cost (USD) | $/annual BTU
Case Study 1 | 56603 | 750000 | 1.325e-05
Case Study 2 | 25717 | 700000 | 2.7219e-05
Case Study 3 | 60507 | 1250000 | 2.0659e-05
Simple average | 47609 | 900000 | 1.8904e-05
This is the cost per unit heat delivered via heat pump. We want the cost per unit energy consumed.
Therefore, we need to take into account the efficiency of heat use.
Efficiency of industrial heat pump
3 | COP | Based on Arpagaus et al. curve, assuming a temperature lift of around 55 C (e.g., industries using waste heat as the heat source, boosting 45 C to 100 C or similar)
Cost per unit of electricity consumed annually:
6.3013e-06 | $/(BTU/yr)
Natural gas boilers
Region | Purchase Price | Natural gas price ($/MMBtu) | Hourly fuel cost ($) | First-Year Total Cost ($)
Midwest | 87540 | 5.37 | 22.47 | 206190
Northeast | 87540 | 7.87 | 32.93 | 261399
South | 87540 | 3.8 | 15.91 | 171567
West | 87540 | 6.2 | 25.94 | 224501
Annual operating hours: | 5280
First-Year cost is capital cost plus the first year of fuel costs.
| First-Year Fuel Cost | First-Year Fuel Use (BTU)
Midwest | 118641.6 | 22093407821.229
Northeast | 173870.4 | 22092808132.1474
South | 84004.8 | 22106526315.7895
West | 136963.2 | 22090838709.6774
This represents the same boiler in different regions, so we should average the minimal differences in fuel use, which may be rounding error in NREL's values)
Capital cost per BTU
3.9618e-06 | $/(BTU/yr)
Industrial fossil fuel boilers
| Reference capacity (kW) | Overnight capital cost (USD/kW) | Boiler cost ($) | Conversion efficiency | Annual Energy Input (BTU) | Cost per annual energy ($/(BTU/yr))
coal (steam boiler) | 2000 | 300 | 600000 | 90% | 40035776000 | 1.4987e-05
petroleum products (steam boiler) | 2000 | 200 | 400000 | 85% | 42390821647.0588 | 9.436e-06
natural gas (steam boiler) | 2000 | 100 | 200000 | 95% | 37928629894.7368 | 5.2731e-06
| Value | Unit
Annual heat output | 10560000 | kWh
Conversion factor | 3412.14 | BTU/kWh
Annual heat output | 36032198400 | BTU
We use NREL's natural gas boiler cost rather than IRENA's cost because it is based on precise figures, while IRENA used round numbers
for their assumptions.
Hydrogen boiler
The ARB document suggests that a hydrogen boiler under a "conservative" scenario would cost
50% more than a natural gas boiler.
5.9427e-06 | $/(BTU/yr)

## Cooling
Natural Gas-Fired Chillers
Based on a 500-ton natural gas-fired absorption chiller
Capital cost | 307500 | $
Operating hours | 4000 | hours/yr
Natural gas charges | 75863 | $
Electricity charges (for pumps) | 6226 | $
Natural gas rate | 0.45 | $/therm
Electricity rate | 0.15 | $/kWh
NG use | 168584.4444 | therms
Electricity use | 41506.6667 | kWh
Conversion factor | 100000 | BTU/therm
Conversion factor | 3412.14 | BTU/kWh
NG use | 16858444444.4444 | BTU
Electricity use | 141626557.6 | BTU
The vast majority of the energy use is natural gas. But we don't want to disregard the
cost of the electricity used to power the pumps. So we sum it with natural gas.
Energy use (over 99% natural gas) | 17000071002.0444 | BTU
Cost per BTU consumed | 1.8088e-05 | $/(BTU/yr)
Electric Chiller
Centrifugal chillers >400 tons
Low-end capital cost | 200 | $/ton
High-end capital cost | 500 | $/ton
Average capital cost | 350 | $/ton
Capacity of reference chiller | 500 | tons | Assumed to be the same as the NG-fired chiller above
Capital cost of electric chiller | 175000 | $
Energy intensity of centrifugal chiller 300 - 600 tons capacity | 0.576 | kW/ton
Power of centrifugal chiller 300 - 600 tons capacity | 288 | kW
Operating hours | 4000 | hours/yr | Assumed to be the same as the NG-fired chiller above
Electricity use | 1152000 | kWh
Electricity use | 3930785280 | BTU
Cost per BTU consumed | 4.452e-05 | $/(BTU/yr)

## IECCpUAEU
Unit: $/(BTU/yr) - dollars of capital cost for equipment per BTU consumed annually by that equipment | electricity if | hard coal if | natural gas if | biomass if | petroleum diesel if | heat if | crude oil if | heavy or residual fuel oil if | LPG propane or butane if | hydrogen if
boilers | 6.3013e-06 | 1.4987e-05 | 3.9618e-06 | 1.4987e-05 | 9.436e-06 | 0 | 9.436e-06 | 9.436e-06 | 9.436e-06 | 5.9427e-06
nonboiler low temp | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
nonboiler med temp | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
nonboiler high temp | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
cooling | 4.452e-05 | 1.8088e-05 | 1.8088e-05 | 1.8088e-05 | 1.8088e-05 | 0 | 1.8088e-05 | 1.8088e-05 | 1.8088e-05 | 1.8088e-05
machine drive | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
electrochemical | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
other processes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Green cells are known explicitly. Orange cells are assumptions based on similar fuel types.